## Combustion Settings History
VALUES
New POL
MAIN MENU DESCRIPTION | SUB_MENU ITEM | PARAMETER | UOM | 2013-01-01 | 2013-01-25 | 2013-01-29 | 2013-05-22 | 2013-08-29 | 2013-09-05 | 2013-09-08
User Setting Menu
|  | Temperature | C | 75 | 80 | 80 | 82 | 81 | 82 | 82
|  | Setting Value | C | 55 | 55 | 55 | 55 | 55 | 55 | 55
Service Setting Menu
Underpressure
|  | Underpressure Setting | Pa | 25 | 25 | 25 | 17 | 25 | 25 | 20
|  | Reduce underpressure | Pa | 8 | 6 | 6 | 6 | 8 | 8 | 8
|  | Offtime | min | 35 | 20 | 35 | 35 | 35 | 35 | 35
O2 Sensor
|  | Setting O2 Concentration | % | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2
|  | O2 Calibration | Status | off | off | off | off | off | off | off
|  | Decreasing Power |  | 10 | 5 | 10 | 10 | 10 | 10 | 10
|  | Increasing Power |  | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | Clear Err Flags |  | off | off | off | off | off | off | off
Fans
Primary fan 1
|  | 30% | % | 50 | 50 | 58 | 57 | 57 | 57 | 57
|  | 40% | % | 56 | 56 | 63 | 64 | 64 | 64 | 64
|  | 50% | % | 62 | 62 | 74 | 70 | 70 | 70 | 70
|  | 60% | % | 68 | 68 | 78 | 80 | 80 | 80 | 80
|  | 70% | % | 70 | 70 | 82 | 85 | 85 | 85 | 85
|  | 80% | % | 78 | 78 | 87 | 88 | 88 | 88 | 88
|  | 90% | % | 82 | 82 | 90 | 92 | 92 | 92 | 92
|  | 100% | % | 85 | 85 | 95 | 97 | 97 | 97 | 97
Secondary fan 1
|  | 30% | % |  | 30 | 45 | 30 | 45 | 45 | 45
|  | 40% | % |  | 32 | 50 | 33 | 50 | 50 | 50
|  | 50% | % |  | 35 | 60 | 40 | 60 | 60 | 60
|  | 60% | % |  | 39 | 65 | 45 | 65 | 65 | 65
|  | 70% | % |  | 45 | 70 | 55 | 70 | 70 | 70
|  | 80% | % | 50 | 50 | 75 | 65 | 75 | 75 | 75
|  | 90% | % | 53 | 53 | 78 | 75 | 78 | 78 | 78
|  | 100% | % | 55 | 58 | 80 | 82 | 80 | 80 | 80
Secondary fan 2
|  | 30% | % | 30 | 60 | 20 | 25 | 25 | 20 | 20
|  | 40% | % | 32 | 65 | 29 | 30 | 30 | 29 | 29
|  | 50% | % | 35 | 70 | 32 | 35 | 35 | 32 | 32
|  | 60% | % | 39 | 80 | 38 | 40 | 40 | 38 | 38
|  | 70% | % | 45 | 90 | 43 | 45 | 45 | 43 | 43
|  | 80% | % | 49 | 92 | 49 | 50 | 50 | 49 | 49
|  | 90% | % | 50 | 95 | 51 | 60 | 60 | 51 | 51
|  | 100% | % | 58 | 95 | 55 | 75 | 75 | 55 | 55
|  | Runout Time | min | 5 |  | 7 | 7 | 7 | 5 | 5
|  | Underpressure Hysteresis | Pa | 12 |  | 12 | 11 | 11 | 12 | 12
Engines
|  | De-ashing Number of charges | ea | 100 | 100 | 150 | 155 | 100 | 100 | 100
|  | De-ashing Time | sec | 60 | 60 | 60 | 200 | 200 | 40 | 40
|  | Burner number of charges | ea | 5 | 5 | 5 | 5 | 20/130 | 130 | 130
|  | Burner Cleaning Time | sec | 15 | 15 | 15 | 265 | 195/240 | 240 | 240
|  | Exchanger number of charges | ea | 100 | 100 | 100 | 100 | 200/100 | 150 | 150
|  | Exchanger Time | sec | 45 | 45 | 20 | 40 | 45 | 45 | 45
Pneumatic Conveyor
|  | M1 Max Time Feeding | min | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | Waiting Time Min Power | min | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15
|  | Wait Time Max Power | min | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5
|  | Clack On Delay | sec | 15 | 15 | 15 | 25 | 15 | 15 | 15
|  | Clack Off Delay | sec | 15 | 15 | 15 | 25 | 15 | 15 | 15
|  | Min Off Time | min | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | PWM On Time | sec | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | PWM Off Time | sec | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  | PWM Number of Attempts | ea | 5 | 5 | 5 | 7 | 5 | 5 | 5
Dampers
|  | Exchanger Temp Open Clack | C | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  | Exchanger Temp Close Clack | C | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | Damper Delay | sec | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | Boiler Temp Close Clack | C | 90 | 90 | 90 | 90 | 93 | 93 | 93
Pumps
|  | Min Boiler temperature | C | 48 | 48 | 48 | 48 | 48 | 48 | 48
|  | Max Boiler Temperature | C | 80 | 80 | 80 | 80 | 80 | 80 | 80
Ignition
|  | Ignition Time | min | 10 | 10 | 10 | 5 | 10 | 10 | 10
|  | Exh Temp ignition | C | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Space Between ignition | sec | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | Ignition Repetition | times | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | Exhaust Against Boiler Temp | status | 0 | 0 | 0 | 0 | 5 | 5 | 5
|  | HysExhmout | K | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | Feeding Between Ignition | % | 50 | 50 | 20 | 20 | 50 | 50 | 50
|  | Hys At open Exchanger | K | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | Lock Ignition at Close Exch Clack | sec | 90 | 90 | 120 | 120 | 90 | 90 | 90
COLD START
|  | Enable Cold Start |  | ON |  | OFF | ON | ON | ON | ON
|  | Feed Cold Start | sec | 5 | 5 | 1 | 1 | 5 | 5 | 5
|  | Cold Start Pause | sec | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | Cold Start Max Time | min | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | Exh Gas Difference | K | 15 | 15 | 15 | 15 | 15 | 15 | 15
UPKEEP MODE
|  | Enable Upkeep Mode | status | OFF | OFF | OFF | ON | OFF | ON | ON
|  | Exhaust | C | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | Exh Hysteresis | K | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | O2 Level | % | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8
|  | Feed Time | sec | 5 | 5 | 5 | 2.5 | 5/2.5 | 2.5 | 2.5
|  | Pause | min | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | Fan Power | % | 65 | 65 | 65 | 65 | 65 | 65 | 65
|  | Time Fan run | sec | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | Lock Ignition After Upkeep | sec | 65 | 65 | 65 | 65 | 65 | 65 | 65
Valves
|  | Open Time | sec | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | Close Time | sec | 120 | 120 | 120 | 120 | 120 | 120 | 120
Power Settings
|  | Max Power Pause | sec | 50 | 50 | 36 | 50 | 36 | 46 | 48
|  | Min Power Pause | sec | 100 | 100 | 100 | 100 | 65 | 75/100 | 100
|  | First Feeding | sec | 12 | 12 | 12 | 20 | 15 | 20 | 20
|  | feeder On Time | sec | 2.5 | 2.5 | 2 | 1.4 | 1.7 | 1.4 | 1.35
kW Max |  | (From Hamont Calculator) | kW | 137 | 137 | 111 | 78 | 130 | 85 | 76
kW Min |  | (From Hamont Calculator) | kW | 70 | 70 | 56 | 40 | 73 | 53 | 38
Diagnostic
Version
|  | BPS Version |  | 9 | 9 | 9 | 9.2 | 9.2 | 9.2 | 9.2
|  | Application Information |  | 30.11.2012 | 30.11.2012 | 30.11.2012 | 30.11.2012 | 30.11.2012 | 30.11.2012 | 30.11.2012
|  |  |  | WS9 | WS9 | WS9 | WS9 | WS9 | WS9 | WS9
|  |  |  | POL 687.0 | POL 687.0 | POL 687.0 | POL 687.0 | POL 687.0 | POL 687.0 | POL 687.0
TCP/IP
|  | DHCP |  | Passive | Passive | Passive | Passive | Passive | Passive | Passive
|  | Actual IP |  | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42
|  | Actual Mask |  | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0
|  | Act Gateway |  | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1
|  | Given IP |  | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42 | 192.168.1.42
|  | Given Mask |  | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0 | 255.255.255.0
|  | Given Gateway |  | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1 | 192.168.1.1
|  | 100 Mbit |  | Active | Active | Active | Passive | Active | Active | Active
|  | Name |  | POL 687_04F6E0 | POL 687_04F6E0 | POL 687_04F6E0 | POL 687_04F6E0 | POL 687_065622 | POL 687_065622 | POL 687_065622
|  | MAC |  | 00-A0-03-04-F6-E0 | 00-A0-03-04-F6-E0 | 00-A0-03-04-F6-E0
|  | Link |  | Active | Active | Active | Passive | Active | Active | Active
|  | User Name |  | ADMIN | ADMIN | ADMIN | ADMIN | ADMIN | ADMIN | ADMIN
|  | Web Password |  | SBTAdmin! | SBTAdmin! | SBTAdmin! | SBTAdmin! | SBTAdmin! | SBTAdmin! | SBTAdmin!
|  | FTP User name |  | ADMIN | ADMIN | ADMIN | ADMIN | ADMIN | ADMIN | ADMIN
Rest
Operating Hours | [7 empty] | 4936
| Act Time Operation |  | hrs | [6 empty] | 174.6
| Act Reduce Time |  | hrs | [6 empty] | 70.9
| Deasching |  | hrs | [6 empty] | 3.6
| Burner Cleaning |  | hrs | [6 empty] | 34.9
| Exchanger Cleaning |  | hrs | [6 empty] | 0.7
| Exchanger Deasching |  | hrs | [6 empty] | 1.1
| Boiler Pump |  | hrs | [6 empty] | 245.2
| Feeder 1 |  | hrs | [6 empty] | 4.7
| Ignition |  | hrs | [6 empty] | 1
| Exhaust Damper |  | hrs | [6 empty] | 244.2

## Hamont kW Calculator
Hamont Fuel Calculator
Change timing F1
Pellets | 250kW
Output calculator |  | fuel 18MJ =5,0 kWh
auger 125mm
gearbox |  | 3600
| F1 on | 1.35 | sec | Konstanta
| F1 off | 100 | sec | 185 | g/s
| cycle | 101.35
|  | 35.5205 | period
|  | 47.9526 | sec | 8.8712 | kg/hod
|  |  |  | 38.3592 | kW
|  |  | Equivalent | 130887.1546 | btu